## Sheet1
INVERSE DEFINITE MINIMUM TIME (Standard Inverse)
Curve Type= | Standard Inverse
α= | 0.02
β= | 0.14
Supply Characteristics
Voltage | 11000 | V
Available Fault | 45 | MVA
Fault Current | 2361.8875 | A
Supply Relay Setting
TMS= | 0.35 | Seconds
V1= | 11000 | V
I1= | 400 | A
Inst1= | 4 | Multiplier
I '1= | 400 | Adjusted to 11000V Base
Relay 1
Clearance 1 = | 0.4 | Seconds
TMS = | 0.4 | Seconds
V1 = | 11000 | V
I1 = | 250 | A
Inst1 = | 5 | Multiplier
I '1 = | 250 | Adjusted to 11000V Base
Relay 2
Clearance 2 = | 0.4 | Seconds
TMS 2 = | 0.5 | Seconds
V2 = | 400 | V
I2 = | 3600 | A
Inst2 = | 6 | Multiplier
I '2 = | 130.9091 | Adjusted to 11000V Base
t=("β" ×TMS)/((I/I_0 )^α-1)

## Sheet3 (hidden)
Fault Current
| 2361.8875 | 0.01
| 2361.8875 | 10
Standard Inverse Curve
| Io/I |  |  |  |  | Io/I |  |  |  |  | Io/I
1 | 1.1 | 440 | 25.6811 | 25.2811 | 1 | 1.1 | 275 | 29.3498 | 28.9498 | 1 | 1.1 | 144 | 36.6872 | 36.2872
2 | 1.39 | 556 | 7.4155 | 7.0155 | 2 | 1.49 | 372.5 | 6.9935 | 6.5935 | 2 | 1.59 | 208.1455 | 7.5125 | 7.1125
4 | 1.68 | 672 | 4.698 | 4.298 | 4 | 1.88 | 470 | 4.4075 | 4.0075 | 4 | 2.08 | 272.2909 | 4.7441 | 4.3441
8 | 2.26 | 904 | 2.9804 | 2.5804 | 8 | 2.66 | 665 | 2.8341 | 2.4341 | 8 | 3.06 | 400.5818 | 3.0946 | 2.6946
12 | 2.84 | 1136 | 2.3228 | 1.9228 | 12 | 3.44 | 860 | 2.2385 | 1.8385 | 12 | 4.04 | 528.8727 | 2.4719 | 2.0719
14 | 3.13 | 1252 | 2.1228 | 1.7228 | 14 | 3.83 | 957.5 | 2.0572 | 1.6572 | 14 | 4.53 | 593.0182 | 2.2819 | 1.8819
15 | 3.275 | 1310 | 2.0408 | 1.6408 | 15 | 4.025 | 1006.25 | 1.9829 | 1.5829 | 15 | 4.775 | 625.0909 | 2.2039 | 1.8039
16 | 3.42 | 1368 | 1.9681 | 1.5681 | 16 | 4.22 | 1055 | 1.9168 | 1.5168 | 16 | 5.02 | 657.1636 | 2.1345 | 1.7345
18 | 3.71 | 1484 | 1.8444 | 1.4444 | 18 | 4.61 | 1152.5 | 1.8043 | 1.4043 | 18 | 5.51 | 721.3091 | 2.0161 | 1.6161
20 | 4 | 1600 | 1.7429 | 1.3429 | 20 | 5 | 1250 | 1.7119 | 1.3119 | 20 | 6 | 785.4545 | 1.9186 | 1.5186
|  | 1600 | 0.01 |  |  |  | 1250 | 0.01 |  |  |  | 785.4545 | 0.01
|  | 1600 | 1.7429 |  |  |  | 1250 | 1.7119 |  |  |  | 785.4545 | 1.9186