## Fault Loop
Fault Loop Impedance
Service Voltage |  |  |  | 230 | V |  | Cable Derating Factor
Frequency |  |  |  | 50 | Hz |  | Temperature Derating Factor |  |  |  | 0.91
No. of Phases |  |  |  | 1 | Φ | [5 empty] | AS/NZS 3008.1 Table 27(1)
Resistivity, ρ |  |  |  | 0.0225 | Ω-mm²/mm |  | Grouping Factor |  |  |  | 0.97
MCB Tripping Current (Note 2) |  |  |  | 7.5 | x IR | [5 empty] | AS/NZS 3008.1 Table 24
Max Cable Length |  |  |  | 2000 | m |  | Total derating factor |  |  |  | 0.8827
Phase CSA. mm² |  |  | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70
PE CSA. mm² |  |  | 2.5 | 2.5 | 2.5 | 4 | 6 | 6 | 10 | 16 | 25
Ampacity (A) |  |  | 26 | 34 | 44 | 60 | 80 | 105 | 130 | 160 | 200
Derated Ampacity (A) |  |  | 22.9502 | 30.0118 | 38.8388 | 52.962 | 70.616 | 92.6835 | 114.751 | 141.232 | 176.54
MCB (A) |  |  | MAXIMUM LENGTH (M)
1 |  |  | 1362.963 | 1677.4929 | 1924.183
2 |  |  | 681.4815 | 838.7464 | 962.0915 | 1557.672
4 |  |  | 340.7407 | 419.3732 | 481.0458 | 778.836 | 1189.4949 | 1318.9964
6 |  |  | 227.1605 | 279.5821 | 320.6972 | 519.224 | 792.9966 | 879.3309 | 1413.4431
10 |  |  | 136.2963 | 167.7493 | 192.4183 | 311.5344 | 475.798 | 527.5986 | 848.0658 | 1321.6611
16 |  |  | 85.1852 | 104.8433 | 120.2614 | 194.709 | 297.3737 | 329.7491 | 530.0412 | 826.0382 | 1255.3606
20 |  |  | 68.1481 | 83.8746 | 96.2092 | 155.7672 | 237.899 | 263.7993 | 424.0329 | 660.8305 | 1004.2885
25 |  |  | : | 67.0997 | 76.9673 | 124.6138 | 190.3192 | 211.0394 | 339.2263 | 528.6644 | 803.4308
32 |  |  | : | : | 60.1307 | 97.3545 | 148.6869 | 164.8746 | 265.0206 | 413.0191 | 627.6803
40 |  |  | : | : | : | 77.8836 | 118.9495 | 131.8996 | 212.0165 | 330.4153 | 502.1442
50 |  |  | : | : | : | 62.3069 | 95.1596 | 105.5197 | 169.6132 | 264.3322 | 401.7154
63 |  |  | : | : | : | : | 75.5235 | 83.7458 | 134.6136 | 209.7875 | 318.8217
80 |  |  | : | : | : | : | : | 65.9498 | 106.0082 | 165.2076 | 251.0721
100 |  |  | : | : | : | : | : | : | 84.8066 | 132.1661 | 200.8577
125 |  |  | : | : | : | : | : | : | : | 105.7329 | 160.6862
Notes:
1. Shaded cells means cable derated current carrying capacity is lower than MCB rating. Blank
cells means that cable length exceeds maximum cable length.
2. Circuit Breaker Trip Current
| Type B | = 4 x rated current
| Type C | = 7.5 x rated current
| Type D | = 12.5 x rated current
3. Current carrying capacities are based on a 75°C PVC Insulated two-core able installed
in air touching.