## Sheet1
INVERSE DEFINITE MINIMUM TIME
Supply Characteristics
Voltage | 11000 | V
Available Fault | 60 | MVA
Fault Current | 3149.1833 | A
Supply Relay Setting
Curve Type= | Extremely Inverse
α= | 2
β= | 80
TMS= | 0.35 | Seconds
VS= | 11000 | V
IS= | 400 | A
INSTS= | 5 | Multiplier
I'S= | 400 | Adjusted to 11000V Base
LTDS= | 0.9 | Seconds
SetS= | 8 | Multiplier
Set'S= | 3200 | Adjusted to 11000V Base
E/F SettingS | 0.25 | x In
E/F High SettingS | 2 | x In
E/F Time SettingS | 0.4 | Seconds
Relay 1
Curve Type1= | Very Inverse
α1= | 1
β1= | 13.5
Clearance1 = | 0.5 | Seconds
TMS = | 0.4 | Seconds
V1 = | 11000 | V
I1 = | 250 | A
INST1 = | 5 | Multiplier
I '1 = | 250 | Adjusted to 11000V Base
LTD1= | 0.8 | Seconds
Set1= | 12 | Multiplier
Set'1= | 3000 | Adjusted to 11000V Base
E/F Setting1 | 0.2 | x In
E/F High Setting1 | 3 | x In
E/F Time Setting1 | 0.3 | Seconds
Relay 2
Curve Type2= | Standard Inverse
α2= | 0.02
β2= | 0.14
Clearance2 = | 0.4 | Seconds
TMS = | 0.5 | Seconds
V2 = | 400 | V
I2 = | 3600 | A
INST2 = | 6 | Multiplier
I '2 = | 130.9091 | Adjusted to 11000V Base
LTD2= | 0.5 | Seconds
Set2= | 16 | Multiplier
Set'2= | 2094.5455 | Adjusted to 11000V Base
E/F Setting2 | 0.3 | x In
E/F High Setting2 | 5 | x In
E/F Time Setting2 | 0.2 | Seconds
𝑡=("β" ×𝑇𝑀𝑆)/((𝐼/𝐼_0 )^𝛼−1)

## Sheet3 (hidden)
Fault Current
| 3149.1833 | 0.01
| 3149.1833 | 10
| Supply Relay |  |  |  |  | Relay 1 |  |  |  |  | Relay 2
| Extremely Inverse Curve |  |  |  |  | Very Inverse Curve |  |  |  |  | Standard Inverse Curve
| Io/I |  |  |  |  | Io/I |  |  |  |  | Io/I
|  | Current | Time | Clearance |  |  | Current | Time | Clearance |  |  | Current | Time | Clearance
1 | 1.1 | 440 | 133.3333 | 132.8333 | 1 | 1.1 | 275 | 54 | 53.6 | 1 | 1.1 | 144 | 36.6872 | 36.2872
2 | 1.49 | 596 | 22.9489 | 22.4489 | 2 | 1.49 | 372.5 | 11.0204 | 10.6204 | 2 | 1.59 | 208.1455 | 7.5125 | 7.1125
4 | 1.88 | 752 | 11.048 | 10.548 | 4 | 1.88 | 470 | 6.1364 | 5.7364 | 4 | 2.08 | 272.2909 | 4.7441 | 4.3441
8 | 2.66 | 1064 | 4.6086 | 4.1086 | 8 | 2.66 | 665 | 3.253 | 2.853 | 8 | 3.06 | 400.5818 | 3.0946 | 2.6946
12 | 3.44 | 1376 | 2.5846 | 2.0846 | 12 | 3.44 | 860 | 2.2131 | 1.8131 | 12 | 4.04 | 528.8727 | 2.4719 | 2.0719
14 | 3.83 | 1532 | 2.0484 | 1.5484 | 14 | 3.83 | 957.5 | 1.9081 | 1.5081 | 14 | 4.53 | 593.0182 | 2.2819 | 1.8819
15 | 4.025 | 1610 | 1.842 | 1.342 | 15 | 4.025 | 1006.25 | 1.7851 | 1.3851 | 15 | 4.775 | 625.0909 | 2.2039 | 1.8039
16 | 4.22 | 1688 | 1.6658 | 1.1658 | 16 | 4.22 | 1055 | 1.677 | 1.277 | 16 | 5.02 | 657.1636 | 2.1345 | 1.7345
18 | 4.61 | 1844 | 1.3826 | 0.88257 | 18 | 4.61 | 1152.5 | 1.4958 | 1.0958 | 18 | 5.51 | 721.3091 | 2.0161 | 1.6161
20 | 5 | 2000 | 1.1667 | 0.66667 | 20 | 5 | 1250 | 1.35 | 0.95 | 20 | 6 | 785.4545 | 1.9186 | 1.5186
| INSTs | 2000 | 0.9 |  |  | INST1 | 1250 | 0.8 |  |  | INST2 | 785.4545 | 0.5
|  | 2000 | 1.1667 |  |  |  | 1250 | 1.35 |  |  |  | 785.4545 | 1.9186
| LTDs | 2000 | 0.9 |  |  | LTD1 | 1250 | 0.8 |  |  | LTD2 | 785.4545 | 0.5
|  | 3149.1833 | 0.9 |  |  |  | 3000 | 0.8 |  |  |  | 2094.5455 | 0.5
| E/F DT | 100 | 0.9 |  |  | E/F DT | 50 | 0.8 |  |  | E/F DT | 39.2727 | 0.5
|  | 100 | 0.4 |  |  |  | 50 | 0.3 |  |  |  | 39.2727 | 0.2
|  | 800 | 0.4 |  |  |  | 750 | 0.3 |  |  |  | 654.5455 | 0.2